## Revision Notes
Goldrush ECS-200 Point-to-Point Wiring Update
Basis | Updated from CAT ECS customer wiring document M0170677-04, Vol 4 of 6 Customer Connection Wiring and Vol 5 of 6 Customer Connection Wiring Continuation, plus existing Goldrush control narrative / close responsibility philosophy.
Design philosophy | Hardwire critical start/stop/trip/close/permissive/status paths. Use ECS-200 Modbus TCP for rich status, metering, diagnostics, alarms, and HMI context.
Breaker close philosophy | ECS-200 may initiate generator breaker close. Physical close circuit shall pass through SEL-700G synchronism-check / close-permissive contact as final hardwired veto before GCB close coil.
Important drafting note | CAT sheets expose functional ECS landing labels and module connector names. Final physical terminal numbers, wire numbers, and exact contact wetting source must be confirmed against the released CAT panel/shop drawings and field terminal schedule before IFC.
Updated | 2026-07-02 13:56 UTC

## Hardwired P2P
Circuit ID | Generator | Signal / Function | Direction | Source Device | Source Terminal / Contact | Intermediate Device / Contact | Destination Device | Destination Terminal / Contact | Cable / Pair | Signal Type | Normal State / Action | Design Note | Status
GEN-200-START | GEN-200 | Remote start / run request | RTAC -> ECS | SEL-3555 RTAC DO or interposing relay | RTAC GEN1_START_REQ contact / TB TBD | Customer interposing relay if required by voltage/current | CAT ECS-200 Main Terminal Block | START with IDI REF / configured remote start input | TBD | Hardwired discrete | Maintained or momentary per CAT configuration | Use hardwire for start permissive/run request. Confirm whether ECS expects dry contact to IDI REF or customer DC wetting. | VERIFY
GEN-200-STOP | GEN-200 | Remote normal stop / soft stop | RTAC -> ECS | SEL-3555 RTAC DO or interposing relay | RTAC GEN1_STOP_REQ contact / TB TBD | Customer interposing relay if required | CAT ECS-200 Main Terminal Block | STOP or SFT-ESTOP/RM-ESTOP path as approved by CAT | TBD | Hardwired discrete | Open/close per CAT stop scheme | Do not use hard E-stop for normal operator stop. Confirm CAT-preferred terminal for remote normal stop. | VERIFY
GEN-200-ESTOP | GEN-200 | Emergency stop chain | Field safety -> ECS | E-stop pushbuttons / safety relay | Field E-stop loop TBD | CAT EIH / safety circuit per Vol 5 | CAT ECS-200 Main Terminal Block / EIH | ESTOP-A, ESTOP-B, ESTOP IN, ESPB, BTRY POS as applicable | TBD | Safety hardwire | Trips/shuts down on open or active E-stop per CAT | Keep independent of RTAC logic. RTAC may monitor status only. Follow CAT Vol 5 E-stop/f-safety circuit exactly. | VERIFY
GEN-200-CLOSE | GEN-200 | Generator breaker close command path | ECS -> SEL -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P2 / CB-CLOSE relay contact, use 11 COM and 14 NO unless NC required | SEL-700G close permissive / sync-check output contact in series | Generator breaker close coil | GCB close coil + / close circuit terminal TBD | TBD | Hardwired control | ECS close output plus SEL permissive energizes close coil | Preferred philosophy: ECS initiates close, SEL-700G is final hardwired veto. Do not bypass SEL sync-check contact. | UPDATED
GEN-200-OPEN | GEN-200 | Generator breaker open command | ECS/RTAC -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P1 / CB-OPEN relay contact, use 11 COM and 14 NO unless NC required | SEL/lockout permissive as required by switchgear design | Generator breaker open coil | GCB open/trip circuit TBD | TBD | Hardwired control | Opens breaker when commanded | Confirm whether ECS-200 or SEL/RTAC owns normal breaker open/unload-open sequence. | VERIFY
GEN-200-TRIP | GEN-200 | Generator breaker shunt trip | ECS / SEL protection -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P6 / SHT-TRIP relay contact, use 11 COM and 14 NO unless NC required | SEL-700G trip / 86 lockout paths as required | Generator breaker shunt trip coil | GCB shunt trip coil TBD | TBD | Hardwired trip | Trips breaker on protective or controller trip | Protection trip paths from SEL-700G/86 shall remain independent and authoritative. ECS trip may be additive. | UPDATED
GEN-200-52A | GEN-200 | Generator breaker closed status | GCB -> ECS/SEL/RTAC | Generator breaker auxiliary contact | 52G a contact / GCB aux TBD | Marshalling TB / isolation as needed | CAT ECS-200 Main or Paralleling TB plus SEL-700G DI | 52G a / CB closed input; CAT labels include 52G a, SH CLOSE, CB status group | TBD | Dry contact status | Closed contact when GCB closed | Return true breaker status to ECS-200 and SEL/RTAC. Do not fake breaker status to satisfy controller. | UPDATED
GEN-200-52B | GEN-200 | Generator breaker open status | GCB -> ECS/SEL/RTAC | Generator breaker auxiliary contact | 52G b contact / GCB aux TBD | Marshalling TB / isolation as needed | CAT ECS-200 Main or Paralleling TB plus SEL-700G DI | 52G b / CB open input; CAT labels include 52G b, SH OPEN, CB status group | TBD | Dry contact status | Closed contact when GCB open | Use both 52a and 52b where available for status agreement and failed-close detection. | UPDATED
GEN-200-CBALM | GEN-200 | Breaker alarm / trip coil status | GCB -> ECS/RTAC | Generator breaker auxiliary/alarm contact | CB alarm / trip circuit monitor TBD | Marshalling TB | CAT ECS-200 Paralleling TB and/or RTAC DI | CB ALM / SH OPEN / SH CLOSE as applicable | TBD | Dry contact status | Alarm contact per breaker | Map to RTAC/HMI blocked-close and breaker-health logic. | VERIFY
GEN-200-AUTO | GEN-200 | ECS in auto/remote available | ECS -> RTAC | CAT ECS-200 Main Terminal Block | R-2 AUTO relay contact, 11 COM / 14 NO or 12 NC as required | RTAC DI marshalling | SEL-3555 RTAC DI | GEN1_ECS_AUTO / remote-ready DI | TBD | Dry contact status | True when ECS is in Auto/Remote | Use for sequence permissive and HMI. Verify relay assignment/configuration in ECS. | UPDATED
GEN-200-RUN | GEN-200 | Engine running status | ECS -> RTAC | CAT ECS-200 Main Terminal Block | RUN RLY or ENG RUN relay/status, contact TBD | RTAC DI marshalling | SEL-3555 RTAC DI | GEN1_RUNNING DI | TBD | Dry contact status | True when engine running | Hardwired running status supports sequence state even during Modbus failure. | UPDATED
GEN-200-ALARM | GEN-200 | Common alarm | ECS -> RTAC | CAT ECS-200 Main Terminal Block | R alarm / ALARM relay contact, 11 COM / 14 NO or 12 NC as required | RTAC DI marshalling | SEL-3555 RTAC DI | GEN1_COMMON_ALARM DI | TBD | Dry contact status | True on common alarm | Detailed alarm list should come through Modbus; common alarm stays hardwired. | UPDATED
GEN-200-SHUTDOWN | GEN-200 | Common shutdown / unavailable | ECS -> RTAC | CAT ECS-200 Main Terminal Block | US SHTDN / ENG FAIL / shutdown relay/status as configured | RTAC DI marshalling | SEL-3555 RTAC DI | GEN1_COMMON_SHUTDOWN DI | TBD | Dry contact status | True on shutdown/trip/unavailable | Use in start/close inhibit and HMI blocked reason. | UPDATED
GEN-200-LOCKOUT | GEN-200 | Switchgear lockout / 86 trip inhibit | SEL/switchgear -> ECS/RTAC | 86 lockout relay / SEL-700G output | 86/a or relay contact TBD | Marshalling TB | CAT ECS-200 input and RTAC DI | ECS digital input TBD; RTAC GEN1_LOCKOUT DI | TBD | Dry contact status | Blocks close/start as designed | Final landing depends on whether CAT provides a configured spare input for lockout; otherwise RTAC/SEL block the close path. | VERIFY
GEN-200-SYNCOK | GEN-200 | SEL-700G close permissive indication | SEL -> RTAC/ECS path | SEL-700G | Sync-check / close permissive output contact and status bit | Series contact in GCB close circuit | RTAC DI/HMI plus close circuit | RTAC GEN1_SEL_SYNC_OK; close path series contact | TBD | Hardwired permissive/status | True when electrical close conditions are acceptable | This is the final close-veto element; expose status to HMI and sequence logic. | UPDATED
GEN-200-MODBUS | GEN-200 | ECS-200 Modbus TCP link | ECS -> RTAC | CAT ECS-200 Ethernet / network manager | ECS-200 Ethernet port / IP TBD | Industrial Ethernet switch | SEL-3555 RTAC Ethernet | RTAC Modbus TCP client to ECS-200 server, port 50200 per Cat register sheet | TBD | Ethernet / Modbus TCP | Poll status, alarms, metering | Do not rely on Modbus alone for critical trip/close/start permissives. | UPDATED
GEN-300-START | GEN-300 | Remote start / run request | RTAC -> ECS | SEL-3555 RTAC DO or interposing relay | RTAC GEN2_START_REQ contact / TB TBD | Customer interposing relay if required by voltage/current | CAT ECS-200 Main Terminal Block | START with IDI REF / configured remote start input | TBD | Hardwired discrete | Maintained or momentary per CAT configuration | Use hardwire for start permissive/run request. Confirm whether ECS expects dry contact to IDI REF or customer DC wetting. | VERIFY
GEN-300-STOP | GEN-300 | Remote normal stop / soft stop | RTAC -> ECS | SEL-3555 RTAC DO or interposing relay | RTAC GEN2_STOP_REQ contact / TB TBD | Customer interposing relay if required | CAT ECS-200 Main Terminal Block | STOP or SFT-ESTOP/RM-ESTOP path as approved by CAT | TBD | Hardwired discrete | Open/close per CAT stop scheme | Do not use hard E-stop for normal operator stop. Confirm CAT-preferred terminal for remote normal stop. | VERIFY
GEN-300-ESTOP | GEN-300 | Emergency stop chain | Field safety -> ECS | E-stop pushbuttons / safety relay | Field E-stop loop TBD | CAT EIH / safety circuit per Vol 5 | CAT ECS-200 Main Terminal Block / EIH | ESTOP-A, ESTOP-B, ESTOP IN, ESPB, BTRY POS as applicable | TBD | Safety hardwire | Trips/shuts down on open or active E-stop per CAT | Keep independent of RTAC logic. RTAC may monitor status only. Follow CAT Vol 5 E-stop/f-safety circuit exactly. | VERIFY
GEN-300-CLOSE | GEN-300 | Generator breaker close command path | ECS -> SEL -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P2 / CB-CLOSE relay contact, use 11 COM and 14 NO unless NC required | SEL-700G close permissive / sync-check output contact in series | Generator breaker close coil | GCB close coil + / close circuit terminal TBD | TBD | Hardwired control | ECS close output plus SEL permissive energizes close coil | Preferred philosophy: ECS initiates close, SEL-700G is final hardwired veto. Do not bypass SEL sync-check contact. | UPDATED
GEN-300-OPEN | GEN-300 | Generator breaker open command | ECS/RTAC -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P1 / CB-OPEN relay contact, use 11 COM and 14 NO unless NC required | SEL/lockout permissive as required by switchgear design | Generator breaker open coil | GCB open/trip circuit TBD | TBD | Hardwired control | Opens breaker when commanded | Confirm whether ECS-200 or SEL/RTAC owns normal breaker open/unload-open sequence. | VERIFY
GEN-300-TRIP | GEN-300 | Generator breaker shunt trip | ECS / SEL protection -> GCB | CAT ECS-200 Paralleling Terminal Block | R-P6 / SHT-TRIP relay contact, use 11 COM and 14 NO unless NC required | SEL-700G trip / 86 lockout paths as required | Generator breaker shunt trip coil | GCB shunt trip coil TBD | TBD | Hardwired trip | Trips breaker on protective or controller trip | Protection trip paths from SEL-700G/86 shall remain independent and authoritative. ECS trip may be additive. | UPDATED
GEN-300-52A | GEN-300 | Generator breaker closed status | GCB -> ECS/SEL/RTAC | Generator breaker auxiliary contact | 52G a contact / GCB aux TBD | Marshalling TB / isolation as needed | CAT ECS-200 Main or Paralleling TB plus SEL-700G DI | 52G a / CB closed input; CAT labels include 52G a, SH CLOSE, CB status group | TBD | Dry contact status | Closed contact when GCB closed | Return true breaker status to ECS-200 and SEL/RTAC. Do not fake breaker status to satisfy controller. | UPDATED
GEN-300-52B | GEN-300 | Generator breaker open status | GCB -> ECS/SEL/RTAC | Generator breaker auxiliary contact | 52G b contact / GCB aux TBD | Marshalling TB / isolation as needed | CAT ECS-200 Main or Paralleling TB plus SEL-700G DI | 52G b / CB open input; CAT labels include 52G b, SH OPEN, CB status group | TBD | Dry contact status | Closed contact when GCB open | Use both 52a and 52b where available for status agreement and failed-close detection. | UPDATED
GEN-300-CBALM | GEN-300 | Breaker alarm / trip coil status | GCB -> ECS/RTAC | Generator breaker auxiliary/alarm contact | CB alarm / trip circuit monitor TBD | Marshalling TB | CAT ECS-200 Paralleling TB and/or RTAC DI | CB ALM / SH OPEN / SH CLOSE as applicable | TBD | Dry contact status | Alarm contact per breaker | Map to RTAC/HMI blocked-close and breaker-health logic. | VERIFY
GEN-300-AUTO | GEN-300 | ECS in auto/remote available | ECS -> RTAC | CAT ECS-200 Main Terminal Block | R-2 AUTO relay contact, 11 COM / 14 NO or 12 NC as required | RTAC DI marshalling | SEL-3555 RTAC DI | GEN2_ECS_AUTO / remote-ready DI | TBD | Dry contact status | True when ECS is in Auto/Remote | Use for sequence permissive and HMI. Verify relay assignment/configuration in ECS. | UPDATED
GEN-300-RUN | GEN-300 | Engine running status | ECS -> RTAC | CAT ECS-200 Main Terminal Block | RUN RLY or ENG RUN relay/status, contact TBD | RTAC DI marshalling | SEL-3555 RTAC DI | GEN2_RUNNING DI | TBD | Dry contact status | True when engine running | Hardwired running status supports sequence state even during Modbus failure. | UPDATED
GEN-300-ALARM | GEN-300 | Common alarm | ECS -> RTAC | CAT ECS-200 Main Terminal Block | R alarm / ALARM relay contact, 11 COM / 14 NO or 12 NC as required | RTAC DI marshalling | SEL-3555 RTAC DI | GEN2_COMMON_ALARM DI | TBD | Dry contact status | True on common alarm | Detailed alarm list should come through Modbus; common alarm stays hardwired. | UPDATED
GEN-300-SHUTDOWN | GEN-300 | Common shutdown / unavailable | ECS -> RTAC | CAT ECS-200 Main Terminal Block | US SHTDN / ENG FAIL / shutdown relay/status as configured | RTAC DI marshalling | SEL-3555 RTAC DI | GEN2_COMMON_SHUTDOWN DI | TBD | Dry contact status | True on shutdown/trip/unavailable | Use in start/close inhibit and HMI blocked reason. | UPDATED
GEN-300-LOCKOUT | GEN-300 | Switchgear lockout / 86 trip inhibit | SEL/switchgear -> ECS/RTAC | 86 lockout relay / SEL-700G output | 86/a or relay contact TBD | Marshalling TB | CAT ECS-200 input and RTAC DI | ECS digital input TBD; RTAC GEN2_LOCKOUT DI | TBD | Dry contact status | Blocks close/start as designed | Final landing depends on whether CAT provides a configured spare input for lockout; otherwise RTAC/SEL block the close path. | VERIFY
GEN-300-SYNCOK | GEN-300 | SEL-700G close permissive indication | SEL -> RTAC/ECS path | SEL-700G | Sync-check / close permissive output contact and status bit | Series contact in GCB close circuit | RTAC DI/HMI plus close circuit | RTAC GEN2_SEL_SYNC_OK; close path series contact | TBD | Hardwired permissive/status | True when electrical close conditions are acceptable | This is the final close-veto element; expose status to HMI and sequence logic. | UPDATED
GEN-300-MODBUS | GEN-300 | ECS-200 Modbus TCP link | ECS -> RTAC | CAT ECS-200 Ethernet / network manager | ECS-200 Ethernet port / IP TBD | Industrial Ethernet switch | SEL-3555 RTAC Ethernet | RTAC Modbus TCP client to ECS-200 server, port 50200 per Cat register sheet | TBD | Ethernet / Modbus TCP | Poll status, alarms, metering | Do not rely on Modbus alone for critical trip/close/start permissives. | UPDATED

## CAT ECS Terminals
CAT Sheet / Area | Functional Label | CAT Device / Relay | Terminal / Contact Shown | Use in Goldrush | Design Treatment | Notes
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | START | Main TB | START / IDI REF / GND group | Remote start/run request from RTAC or approved start circuit | Hardwired control | Confirm dry-contact vs wetted input and maintained/momentary behavior.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | STOP | Main TB | STOP | Remote normal stop if supported/configured | Hardwired control | Use normal stop, not hard E-stop, for operator stop sequence.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | ESTOP IN / ESTOP OUT / ESTOP-A / ESTOP-B / SFT-ESTOP / RM-ESTOP | Main TB / safety circuit | E-stop labels plus Vol 5 wiring | Emergency shutdown chain and status | Safety hardwire | Do not route safety dependency through RTAC logic.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | AUTO | R-2 | 11 COM / 14 NO / 12 NC | ECS in Auto/remote status to RTAC | Hardwired DI | Use as sequence permissive.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | ALARM | R-1 or configured alarm relay | 11 COM / 14 NO / 12 NC | Common ECS alarm to RTAC/HMI | Hardwired DI | Detailed alarms via Modbus.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | RUN RLY / ENG RUN | Configured relay/status | Contact/terminal label shown | Generator running status | Hardwired DI | Use to qualify sequence state.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | ENG FAIL / US SHTDN | Configured relay/status | Contact/terminal label shown | Shutdown/unavailable inhibit | Hardwired DI | Use for blocked start/close reason.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | 52G a / 52G b | Breaker aux status inputs | 52G a, 52G b labels | Generator breaker closed/open feedback | Hardwired status | Return real breaker status to ECS and SEL/RTAC.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | RRAUX / LFAUX groups | Breaker auxiliary groups | RRAUX-NO/NC/COM; LFAUX-NO/NC/COM | Breaker aux interface if applicable | Hardwired status | Confirm which group maps to Goldrush GCB implementation.
Sheet 13 Main Terminal Block CAT ECS-100 and 200 | RR-CLOSE / RR-OPEN / RR-TRIP; LF-CLOSE / LF-OPEN / LF-TRIP | Breaker control groups | Control labels shown | Breaker control if configured on main TB | Hardwired control | Paralleling TB Sheet 16 appears more directly applicable for ECS-200 paralleling close/open/trip.
Sheet 14 A6L3 Control Module | A6L3-200 J1 | Paralleling control module | J1 pins 1-20, DI and DI REF groups | Internal/controller I/O reference | Reference only | Do not field-land directly unless CAT directs; use provided terminal blocks.
Sheet 14 A6L3 Control Module | A6L3-200 J2 | Paralleling control module | J2 pins 1-16, analog/PWM/CAN items | Internal/controller I/O reference | Reference only | Use terminal blocks or vendor harness where supplied.
Sheet 14 A6L3 Control Module | A6L3-200 J4 | Paralleling control module | J4 pins 1-16 | Internal/controller I/O reference | Reference only | A6L3 module shown to identify underlying I/O.
Sheet 15 CAT Connect | Ethernet / telematics | A6N1H/A6N2, PL243V3/PLCN1 | RJ45 / 10/100BASE-T labels | Telemetry/network only if used | Communications | Not primary RTAC/ECS interface unless Cat telematics is in scope.
Sheet 16 Paralleling Terminal Block CAT ECS-200 | CB-CLOSE | R-P2 | Relay contact 11 COM / 14 NO / 12 NC | ECS generator breaker close output | Hardwired control | Route through SEL-700G sync-check/close permissive contact before GCB close coil.
Sheet 16 Paralleling Terminal Block CAT ECS-200 | CB-OPEN | R-P1 | Relay contact 11 COM / 14 NO / 12 NC | Generator breaker open output | Hardwired control | Confirm owner of normal open/unload-open sequence.
Sheet 16 Paralleling Terminal Block CAT ECS-200 | SHT-TRIP | R-P6 | Relay contact 11 COM / 14 NO / 12 NC | Generator breaker shunt trip output | Hardwired trip | SEL protection/86 trip path remains independent.
Sheet 16 Paralleling Terminal Block CAT ECS-200 | AUX1/AUX2/AUX3/AUX4 | R-P7 through R-P12 / aux relays | AUXx-NO/NC/COM | Spare/aux ECS statuses or controls | Configurable hardwire | Assign only after confirming ECS relay configuration.
Sheet 16 Paralleling Terminal Block CAT ECS-200 | DI REF A/B/C/D, BTRY POS/NEG | Paralleling TB | DI reference and battery power groups | Reference/power for ECS discrete I/O | Power/reference | Do not mix external supplies without CAT approval.
Vol 5 E-stop & Functional Safety | E-stop / functional safety diesel and gas | EIH harness / A6L3 GEN / A6L3 paralleling | ESTOP-A/B, ESPB, RST1, DO-6, R-P3, R4/R5 | Safety shutdown and reset circuit | Safety hardwire | Follow CAT circuit exactly. This sheet is not a general-purpose RTAC control landing area.
Vol 5 CAN circuit | CAN 1 / CAN 2 | GEN A6L3, PARALLEL A6L3, optional modules | CAN + / CAN - / SH | CAT internal/controller network | Vendor network | Maintain shield/termination per CAT; not a substitute for RTAC Modbus TCP.
Vol 5 Ethernet circuit | 4-wire / 2-wire Ethernet | GEN A6L3, PARALLELING A6L3, HMI, telematics | Ethernet port labels | ECS network / HMI / service / RTAC Modbus path | Communications | Confirm IP addressing and switch topology.
Vol 5 Multiple Genset Paralleling | APCDL / 4-wire Ethernet | A6L3 paralleling modules | Unit 01-04 example, up to 26 gensets | GEN-200/GEN-300 paralleling data/control | Vendor network | Use CAT-required architecture for generator-to-generator paralleling; RTAC supervises but should not replace CAT load-share network.

## Modbus Network
Point Group | Source | Destination | Protocol | Use | Do Not Use For | Notes
ECS metering | ECS-200 | SEL-3555 RTAC / HMI | Modbus TCP, port 50200 per Cat register sheet | Voltage, current, kW, kVAR, PF, frequency, phase angle, bus/generator sync values | Protection-grade decisions or sole close permissive | Use for display and sequence context with quality/timeouts.
Engine/package status | ECS-200 | SEL-3555 RTAC / HMI | Modbus TCP | RPM, oil pressure, coolant temp, battery voltage, runtime, starts count | Safety shutdown chain | Display and alarm enrichment.
Detailed alarms/events | ECS-200 | SEL-3555 RTAC / HMI | Modbus TCP | Detailed warning/shutdown/event text or codes | Only hardwired alarm/shutdown indication | Common alarm/shutdown stays hardwired.
Control writes | SEL-3555 RTAC | ECS-200 | Modbus TCP writes if enabled | Alarm acknowledge, reset, supervised noncritical commands only | Primary start, stop, trip, close, sync authority | Any writes need operator confirmation, permissives, comms health, and commissioning validation.
SEL relay data | SEL-700G / SEL-751 | SEL-3555 RTAC | SEL protocol / Mirrored Bits / DNP as selected | Protection status, sync-check status, targets, breaker state, relay health | Replacing hardwired trip/close permissive where protection-grade contact is required | Use relay data to drive HMI blocked reasons.
Station integration | SEL-3555 RTAC | Existing SEL-3530 RTAC / SCADA | DNP3 or agreed protocol | Curated system status, alarms, sequence state, UFLS state | Duplicating generator sequence control authority | Existing RTAC should see status and high-level commands only as designed.

## Open Items
ID | Open Item | Why It Matters | Needed From | Suggested Resolution
OI-01 | Confirm final CAT terminal strip physical numbers for each functional label. | M0170677 labels functions but final field drawings may assign terminal numbers/wire numbers. | CAT / panel shop | Request ECS-200 terminal schedule/shop drawing for GEN-200 and GEN-300 panels.
OI-02 | Confirm remote start input wiring method: dry contact to IDI REF versus customer DC wetting. | Incorrect wetting/reference can damage inputs or fail to start. | CAT | Ask for approved remote start wiring detail for ECS-200 retrofit.
OI-03 | Confirm remote normal stop terminal/function. | STOP, SFT-ESTOP, RM-ESTOP, and E-stop labels are not interchangeable. | CAT / controls engineer | Use normal stop for operator stop and reserve E-stop chain for safety.
OI-04 | Confirm ECS-200 breaker close/open/trip ownership and timing. | Close circuit must coordinate with SEL-700G sync-check and avoid nuisance failed-close alarms. | CAT + SEL + owner | Approve ECS close output through SEL contact, with timing in commissioning test.
OI-05 | Confirm 52a/52b auxiliary contact availability and whether contacts can feed ECS and SEL/RTAC separately. | Both systems need real breaker feedback. | Switchgear vendor / field verification | Use separate aux contacts or interposing relays; avoid parallel-loading one contact without review.
OI-06 | Confirm SEL-700G output contact ratings and fail-safe contact logic for close permissive. | Final close-veto contact must be correctly rated and wired normally open/closed by design. | SEL / engineer | Select contact, settings logic, and terminal numbers in relay drawing.
OI-07 | Confirm ECS-200 network architecture/IP addresses and whether CAT paralleling Ethernet/APCDL is isolated from RTAC Modbus network. | Avoid disrupting Cat paralleling/load-share network. | CAT / IT / controls | Use managed switch/VLAN or separate NIC as needed; document IP plan.
OI-08 | Confirm whether the Cat telematics equipment is in scope. | Telematics wiring may be present but not required for RTAC integration. | Owner / CAT | Mark Cat Connect/telematics as by CAT unless HEE scope includes it.
OI-09 | Confirm GEN-200 and GEN-300 nomenclature against actual breaker labels F-240 and F-310. | Prevents cross-wiring between generators. | Owner / field verification | Use one naming standard in all drawings, HMI, RTAC tags, and wire labels.

## Commissioning Checks
Check ID | Circuit | Test | Expected Result | Pass/Fail | Notes
C-01 | Remote start | Assert RTAC start request with ECS in Auto and no lockout. | ECS sees start input and starts generator; RTAC sees running via hardwire and Modbus.
C-02 | Normal stop | Issue RTAC/operator normal stop after unload/open sequence. | ECS performs normal stop/cooldown without invoking E-stop path.
C-03 | E-stop | Operate field E-stop. | ECS hard shutdown path operates independent of RTAC; RTAC/HMI alarms E-stop.
C-04 | Close permissive made | With generator synchronized and SEL sync-check true, assert ECS close output. | Close coil energizes through SEL permissive, breaker closes, 52a/52b feedback agrees.
C-05 | Close permissive blocked | Force SEL sync-check false and assert ECS close output under test conditions. | SEL contact blocks close coil; breaker remains open; HMI shows blocked reason.
C-06 | Breaker feedback | Toggle 52a/52b / simulate breaker open and closed. | ECS, SEL, and RTAC all show correct open/closed status with no disagreement.
C-07 | Trip path | Trip from SEL-700G and separately from ECS shunt trip output where applicable. | Breaker trips; ECS/RTAC/HMI report trip/shutdown/alarm correctly.
C-08 | Modbus loss | Disconnect ECS Modbus link while hardwired statuses remain. | RTAC alarms comms fail, holds/blocks noncritical automation, hardwired safety/control indications remain available.
C-09 | Alarm/shutdown status | Create ECS common alarm/shutdown test point or simulation. | Hardwired common alarm/shutdown and detailed Modbus alarm both map correctly.
C-10 | Network separation | Verify CAT paralleling/load-share network and RTAC polling network operation. | No CAT network faults; RTAC polling stable; IP addresses documented.