Goldrush Generator Integration

Generator Breaker Close Responsibility Philosophy

Draft philosophy for ECS-200, SEL-700G, and RTAC responsibility during generator breaker close and synchronization.

# Purpose

This document captures the recommended responsibility split for closing the Goldrush generator breakers. The approach reconciles the CAT/ECS-200 need to issue the close command and see breaker feedback with the SEL preference that the SEL-700G provide protection-grade synchronism-check and final close supervision.

# Recommended Philosophy

Allow the ECS-200 to initiate the generator breaker close command, but route the physical close circuit through SEL-700G permissive/synchronism-check contacts. The ECS-200 remains responsible for machine control and receives real breaker status feedback. The SEL-700G remains the final electrical permissive/veto device for breaker closing.

ECS-200 controls generator start, warmup, speed, voltage, synchronizing behavior, load control, unload, cooldown, and package alarms/shutdowns.

ECS-200 may issue the generator breaker close output when it believes the generator is ready to close.

SEL-700G provides generator protection, synchronism-check supervision, close permissive, trip targets, event records, and the hardwired final veto in the close circuit.

RTAC coordinates the operator sequence, validates supervisory permissives, and shows blocked-close reasons on HMI.

Do not use Modbus writes or HMI-only logic as the sole final authority for closing the generator breaker.

# Preferred Close Circuit Concept

Preferred hardwired concept:

ECS-200 close output -> SEL-700G sync-check / close permissive contact -> Generator breaker close coil

Breaker 52a/52b status should return to both ECS-200 and SEL/RTAC logic:

Generator breaker 52a / 52b -> ECS-200

Generator breaker 52a / 52b -> SEL-700G / RTAC

# Responsibility Matrix

| System | Responsibility | Notes |
| --- | --- | --- |
| CAT ECS-200 | Machine control and close-command initiation. | Controls speed/voltage and issues close output only after its generator package conditions are satisfied. |
| SEL-700G | Protection-grade close permissive and final hardwired veto. | Uses sync-check and protection logic to allow or block the physical close circuit. |
| SEL RTAC | Sequence coordinator and HMI/block-reason owner. | Requests/permits sequence progress, validates supervisory conditions, and records why the close is blocked. |
| Generator Breaker | Executes close only when close coil circuit is complete. | 52a/52b feedback must be wired and mapped accurately to ECS, SEL, and RTAC. |
| Operator/HMI | Supervisory command and visibility. | Operator should see sequence state, sync status, close permissive, and blocked reason before command execution. |

# Normal Close Sequence

RTAC confirms generator start/close sequence is requested and allowed.

ECS-200 starts generator and controls warmup, speed, and voltage.

RTAC and SEL-700G verify generator breaker open, no lockout, healthy breaker close/trip circuits, and valid voltage references.

ECS-200 brings the generator into synchronizing range and asserts its close output when ready.

SEL-700G sync-check / close permissive contact is already made or closes when electrical conditions are acceptable.

Generator breaker close coil energizes only if ECS close output and SEL-700G permissive path are both true.

Generator breaker closes and real 52a/52b feedback returns to ECS-200, SEL-700G, and RTAC.

RTAC confirms breaker closed, clears close request, records event, and transitions to parallel/load-control state.

ECS-200 handles load acceptance / load sharing / package control after breaker closure.

# Blocked-Close Handling

If the SEL-700G blocks the close circuit, the ECS-200 may see that it issued close but the breaker did not close. This is acceptable and truthful, but normal sequence logic should avoid nuisance failed-close attempts by only allowing the ECS close attempt after the RTAC and SEL status indicate close permissive is already available.

Do not fake breaker-closed feedback to the ECS-200 except under a separately engineered/tested vendor-approved interface requirement.

Show the actual blocked reason on HMI: sync-check fail, voltage mismatch, frequency/slip/angle out of range, lockout active, breaker not available, VT failure, comms fail, or sequence not armed.

Use adjustable timing to avoid CAT controller nuisance alarms if a close permissive is not yet ready.

Require breaker status agreement before transition to load-control state.

# Required Inputs / Status Points

Generator breaker 52a closed status.

Generator breaker 52b open status.

Generator breaker spring charged / close circuit health where available.

Trip circuit monitor and lockout status.

SEL-700G sync-check permissive.

SEL-700G relay health, alarm, time quality, and protection target status.

ECS-200 generator ready/running/available status.

ECS-200 close command active/status if available.

RTAC close request, close enable, blocked reason, and sequence state.

# HMI Requirements

Show generator breaker status from validated 52a/52b feedback.

Show ECS-200 close command/request status.

Show SEL-700G sync-check permissive and close permissive status.

Show active blocked-close reason in plain language.

Show sequence state: idle, starting, synchronizing, close requested, breaker closed, load control, blocked, failed close.

Show trip/lockout status separately from sync-check block status.

Do not provide direct HMI close commands without permissions, confirmation, and hardwired permissive paths.

# Engineering / Commissioning Notes

Confirm CAT/ECS-200 requirements for close output timing and breaker feedback timing.

Confirm SEL-700G contact rating, wiring method, and fail-safe behavior in the close circuit.

Confirm whether close permissive is a maintained permissive contact, pulse-permissive path, or close-supervision contact arrangement.

Point-to-point test ECS close output, SEL permissive contact, breaker close coil path, 52a/52b feedback, and RTAC/HMI indications.

Simulate SEL sync-check block and confirm ECS/RTAC/HMI behavior is acceptable.

Document final close responsibility in the control narrative, schematics, cause-and-effect matrix, and commissioning test script.

Draft status: For project discussion and basis-of-design development. Final implementation requires owner, CAT, SEL, and engineering review.