Goldrush Generator Integration

RTAC-Supervised UFLS Control Scheme

Draft control philosophy for non-sub-cycle staged load shedding during generator island operation.

# Purpose

This document captures the recommended underfrequency/load-shed control scheme for the Goldrush generator integration. The scheme is intended for supervised staged load shedding during islanded generator operation. It is not intended to replace protection-speed or sub-cycle relay UFLS where that level of performance is required.

# Recommended Architecture

Use the SEL RTAC as the supervisory UFLS coordinator and HMI/state-machine owner. Use SEL relays and/or hardwired breaker paths to execute feeder trips. CAT/ECS-200 controls remain responsible for generator package control, speed/voltage response, load control behavior, alarms, and shutdowns.

RTAC determines when UFLS is armed and when a load-shed stage is required.

SEL-751 feeder relays provide feeder breaker status, load/metering, trip target information, relay health, and trip output paths where used.

SEL-700G generator relays provide generator electrical status, protection targets, frequency, generator breaker status, and relay health.

ECS-200 provides generator running/available status, kW, alarms, shutdowns, and package health.

HMI provides clear island status, active UFLS stage, feeder shed state, restore readiness, and blocked reasons.

# Operating Intent

Only arm automatic staged load shedding after island mode is confirmed.

Use both frequency and generator loading/load-margin conditions to determine the need to shed load.

Trip feeders by predefined priority/stage assignment rather than ad hoc operator judgment during an event.

After each stage, verify breaker open feedback and actual load reduction before deciding whether to escalate.

Prefer operator-confirmed restore until final automatic restore philosophy is approved and tested.

Do not automatically restore load if generator alarms, insufficient reserve, frequency instability, or breaker status disagreement exists.

# UFLS Arming Conditions

Island mode confirmed by RTAC.

At least one generator breaker closed and generator source valid.

Utility source is unavailable, separated, or not the active source for the island.

Island bus voltage and frequency are valid.

Required SEL relay communications and breaker status points are healthy.

Required ECS-200 generator status and load information are healthy enough for the selected mode.

No active maintenance/test block on the UFLS scheme.

Feeder trip paths are available or their unavailable condition is clearly shown on HMI.

# Suggested Stage Logic

| Stage | Typical Trigger | Action | Verification |
| --- | --- | --- | --- |
| Stage 1 | Bus frequency below 59.5 Hz for adjustable delay, or generator load above warning threshold for adjustable delay. | Trip lowest-priority noncritical feeders. | Confirm breaker open and measurable kW relief. |
| Stage 2 | Frequency below 59.2 Hz, or Stage 1 fails to recover frequency/load margin within escalation timer. | Trip second-priority feeders. | Confirm breaker open and load reduction before clearing stage request. |
| Stage 3 | Frequency below 58.8 Hz, critical overload, or continued decay after Stage 2. | Aggressive shed to preserve generator stability and essential loads. | Confirm feeder trips and alarm if expected relief is not achieved. |
| Optional Stage 4 | Generator preservation threshold or owner-approved last-resort condition. | Trip additional nonessential feeders before generator protective trip. | Require engineering/owner approval before enabling. |

# RTAC Sequence

Confirm island mode and validate bus frequency source.

Calculate generator online capacity, generator total kW, reserve margin, and feeder availability.

Arm UFLS when all arming permissives are true.

Monitor frequency, generator load, rate of recovery, generator alarms, and stage timers.

When a stage trigger is met, assert the corresponding feeder shed request(s).

Trip the selected feeder breakers through the approved SEL relay or hardwired trip path.

Verify breaker open feedback and load reduction.

If frequency/load margin recovers, hold the current shed state and block auto-restore until stable.

If the system does not recover, escalate to the next stage after the adjustable timer.

Alarm any failed trip, status mismatch, stale data, or no-load-relief condition.

Enable operator-confirmed restore only after all restore permissives are true.

# Core RTAC Tags

UFLS_ARMED

UFLS_ISLAND_CONFIRMED

UFLS_ACTIVE_STAGE

UFLS_STAGE_1_ACTIVE / UFLS_STAGE_2_ACTIVE / UFLS_STAGE_3_ACTIVE

UFLS_TOTAL_KW_SHED

UFLS_ESCALATION_TIMER

UFLS_RESTORE_READY

UFLS_RESTORE_BLOCK_REASON

UFLS_LOAD_SHED_FAILED

FEEDER_x_SHED_REQUEST

FEEDER_x_SHED_COMPLETE

FEEDER_x_RESTORE_PERMISSIVE

FEEDER_x_RESTORE_BLOCK_REASON

# Restore Philosophy

Initial restore should be operator-confirmed and staged. Automatic restore may be added later only after owner approval, test experience, and clear acceptance criteria.

Require frequency recovered and stable for an adjustable timer.

Require generator load below restore threshold with adequate spinning reserve.

Require no active generator alarm/shutdown condition affecting load acceptance.

Require feeder breaker and relay communications healthy.

Restore one feeder or one stage at a time.

After each restore, verify frequency and generator load remain stable before allowing the next restore step.

Block restore if breaker status disagrees, load margin is insufficient, utility restoration is in progress, or generator alarms are active.

# HMI Requirements

Show island mode status, UFLS armed status, bus frequency, generator kW, available reserve, and active stage.

Show each feeder with stage assignment, current kW, breaker status, trip-path status, and shed/restored state.

Show next feeder/stage to trip before a stage is active.

Show why UFLS is blocked, why restore is blocked, and whether data quality is stale or failed.

Show failed-trip or no-load-relief alarms distinctly from normal shed actions.

Keep command buttons separate from indication. Restore commands should require confirmation and permission.

# Testing / Commissioning Notes

Bench-test each stage trigger, timer, and escalation condition before field commissioning.

Point-to-point verify every feeder trip command and breaker open/closed feedback.

Simulate failed feeder trip, stale relay data, failed load relief, and generator alarm blocks.

Verify event logging and HMI blocked-reason text for each scenario.

Confirm final stage assignments with the owner based on actual feeder criticality and island load study.

Keep all initial threshold and timer values adjustable but access-controlled.

Draft status: For project discussion and basis-of-design development. Final implementation requires owner, SEL, CAT, and engineering review.