Goldrush Generator Project

SEL-700G Recommended Part Number Basis

Revised without RTD card - 2026-07-02 15:02 UTC

# Recommendation

Recommended relay family: SEL-700G1+ generator protection relay, not SEL-700GT.

Recommended order basis without RTD card: 0700G1A1A62CA4A0X851

Change from prior draft: The 10 RTD input card was removed because the ECS-200/CAT package is expected to protect the generator thermal functions. The SEL-700G remains focused on electrical generator protection, synchronism-check, breaker close permissive, trip/status, and RTAC integration.

Important note: This is a quote/design basis part number. SEL should validate the final ordering string before purchase against the latest model option table, project CT/PT ratios, control voltage, communications standard, panel layout, and owner preferences.

# Why SEL-700G1+

The Goldrush generator relays are intended to protect and supervise the two generator breakers, not act only as intertie relays.

SEL-700G1+ provides the generator-focused feature set, including generator differential and generator synchronism/sync-check/autosynchronizer functions.

SEL-700GT is better aligned with intertie protection. It is not the preferred model for the G-200 / G-300 generator breaker relays.

The project philosophy keeps the ECS-200 responsible for machine/package control while the SEL-700G provides protection-grade close permissive and final hardwired sync-check veto in the close circuit.

# Recommended Option Basis

| Option Area | Recommended Basis | Reason / Notes |
| --- | --- | --- |
| Relay model | SEL-700G1+ | Full generator protection basis for G-200 and G-300 generator breaker relays. |
| Front panel | 5 in color touchscreen | Matches modern SEL HMI preference and gives better local commissioning visibility. |
| Power supply | 110-250 Vdc / 110-240 Vac | Wide-range SEL supply. Confirm against station battery / panel control power. |
| Digital input voltage | 125 Vdc/Vac | Assumed to match typical switchgear control voltage and the attached SEL-751 basis. |
| Ethernet | Dual copper Ethernet | Recommended for generator automation backbone, RTAC integration, and future network flexibility. |
| Protocol | DNP3 option; Modbus TCP included with Ethernet per SEL ordering notes | DNP3 is useful for RTAC/SCADA integration. IEC 61850 is not required unless owner standard demands it. |
| I/O expansion | 4 DI / 4 DO fast high-current output card plus 14 DI card | Supports breaker close permissive, trip/status, lockout, ECS-200 interface, and spare commissioning points. |
| RTD inputs | Not included | ECS-200/CAT package is expected to protect generator thermal functions. Add SEL RTD card only if owner wants independent SEL thermal monitoring. |
| Current/voltage inputs | 5 A phase CTs + 5 A neutral CT + 3-phase 300 Vac voltage input | Assumed conventional CT/PT basis. Change if CTs are 1 A or voltage inputs differ. |
| Conformal coating | Yes | Recommended for mine/switchgear environment and aligns with a conservative reliability basis. |

# Quote Language

Suggested quote request wording:

Two SEL-700G1+ generator protection relays, touchscreen, 125 Vdc control input basis, 5 A CT / 300 Vac PT inputs, generator autosynchronizer/sync-check, DNP3, dual copper Ethernet, conformal coating, no RTD input card, with sufficient DI/DO for breaker close permissive, trip, 52a/52b, lockout, ECS-200 interface, and RTAC integration.

# Open Items Before Purchase

Confirm actual generator CT secondary rating: 5 A assumed; change option if 1 A CTs are used.

Confirm available PT secondary voltage and whether the relay needs generator voltage, bus/sync voltage, or both through the selected input option.

Confirm station control voltage and wetting voltage for relay digital inputs.

Confirm whether owner wants IEC 61850 or EtherNet/IP in addition to DNP3/SEL protocols.

Confirm CAT/ECS-200 is the sole required generator thermal protection path; add SEL RTD inputs only if independent thermal monitoring is required.

Confirm panel cutout, mounting accessories, labels, and any SEL wire termination kit requirements.

# References

SEL-700G product page: https://selinc.com/products/700G/

SEL-700G documents page: https://selinc.com/products/700G/docs/

SEL-700G model option table / ordering information: https://selinc.com/api/download/7583/